****

**Aerovent Guide Specification
Fiberglass, Centrifugal Wall Ventilators: Model ASA, Direct Drive**

**Aerovent Model ASA Series, Fiberglass Centrifugal Wall Ventilators** provide a line of quiet, efficient and economical centrifugal wall ventilators designed to offer value and long-lasting service in a wide variety of commercial and industrial ventilating applications.

The Fiber-Aire® ASA fiberglass centrifugal wall ventilator fans are available as direct drive for general ventilation requirements where a low noise level exhaust is desired. The fiberglass housing of this fan is virtually dent, crack, and break proof and is highly resistant to a wide array of chemicals. The motor is completely separated from the airstream.

The fiberglass housing actually absorbs noise and vibration, and the specially molded throat and outlet designs minimize loss from friction and turbulence.

Model ASA (Direct Drive) features fiberglass construction. These units are all designed for wall mounted exhaust.

**Application**

The Fiber-Aire Series ASA fiberglass wall ventilators are ideal for applications where exhausting from the roof is impractical or impossible. Model ASA utilizes a PVC coated bird screen at the fan discharge within the fiberglass enclosure.

Accessibility: All fans feature a heavy duty removable, fiberglass cover. The easily removable covers provide access to fan motor.

Sizes (wheel diameters): 7 to 14 inches (178 mm to 356 mm)

Airflow: Up to 2,230 CFM (3,789 m3/hour)

Static Pressure: Up to 1 inches wg (248 Pa)

Aerovent is a leading designer and manufacturer of high quality industrial air moving equipment. Aerovent has extensive industry experience and years of active research, offering customers flexibility in fan design and construction along with superior service and state-of-the-art technology. With an unmatched variety of axial impellers and centrifugal fan wheels, every fan is built to the customer’s specific needs. This comprehensive selection of products and materials makes Aerovent the ideal choice for a diverse range of industry applications, including: Pulp & Paper, Automotive, Metal & Minerals, Mining, Power Generation, Agricultural, Marine and Water Treatment.

Aerovent occupies over 1,000,000 sq. ft. of manufacturing space in the U.S. Headquarters are located in Minneapolis, Minnesota, which houses the management, sales and marketing, accounting, human resources, material management, engineering personnel, as well as a state-of-the-art AMCA accredited testing lab.

We recommend you consult with your Aerovent Sales Representative, who can be contacted through: Aerovent, Minneapolis MN; (763) 551-7500; email: aerovent\_sales@aerovent.com; [www.aerovent.com](http://www.tcf.com).

This document Copyright© 2017 Aerovent.

SECTION 23 34 23.05 – CENTRIFUGAL WALL VENTILATORS

1. GENERAL
	* + 1. SUMMARY
				1. Section includes fiberglass centrifugal wall ventilators, direct-driven.
			2. REFERENCE STANDARDS
				1. Air Movement and Control Association International, Inc. (AMCA): [www.amca.org](http://www.amca.org):

AMCA Standard 204 - Balance Quality and Vibration Levels for Fans

AMCA Standard 210 -  ASHRAE 51 - Laboratory Methods of Testing Fans for Certified Aerodynamic Performance Rating

AMCA Standard 300 - Reverberant Room Method for Sound Testing of Fans

* + - * 1. ASTM International (ASTM): [www.astm.org](http://www.astm.org):

ASTM E84 - Standard Test Method for Surface Burning Characteristics of Building Materials

* + - * 1. National Electrical Manufacturers Association (NEMA): [www.nema.org](http://www.nema.org):

NEMA MG 1 – Motors and Generators

* + - * 1. National Fire Protection Association (NFPA): [www.nfpa.org](http://www.nfpa.org):

NFPA 70 - National Electric Code

* + - 1. ACTION SUBMITTALS
				1. Product Data: Include the following:

Rated capacities and operating characteristics.

Fan Performance Data: Fan performance curves with flow, static pressure and horsepower.

Sound Performance Data: Fan sound power levels in eight octave bands and, A-weighted overall sound power level or sone values.

Motor ratings and electrical characteristics.

Furnished specialty components.

Specified accessories.

Dimensioned standard drawings indicating dimensions, weights, and attachments to other work.

Specifier: If Contractor will be required to provide engineering drawings and calculations for vibration, seismic, or high wind design, insert requirements here.

* + - 1. INFORMATIONAL SUBMITTALS
				1. Source quality-control reports.
				2. Field quality-control reports.
				3. ISO-9001 certificate.
			2. CLOSEOUT SUBMITTALS
				1. Operation and Maintenance Data: Include routine maintenance, adjustment requirements, safety information, and troubleshooting guide.
			3. QUALITY ASSURANCE
				1. Manufacturer Qualifications: Approved ISO 9001-compliant manufacturer listed in this Section with minimum 10 years' experience in manufacture of similar products in successful use in similar applications, and with an ASME NQA-1 compliant Program.

Specifier: Retain paragraph below if Owner allows substitutions but requires strict control over qualifying of substitutions.

Approval of Comparable Products: Submit the following in accordance with project substitution requirements, within time allowed for substitution review:

Product data, including certified independent test data indicating compliance with requirements.

Project references: Minimum of 5 installations not less than 5 years old, with Owner contact information.

Sample warranty.

Substitutions following award of contract are not allowed except as stipulated in Division 01 General Requirements.

Approved manufacturers must meet separate requirements of Submittals Article.

* + - * 1. AMCA Compliance:

Provide fan types tested in accordance with AMCA Standard 210 (air performance) and AMCA Standard 300 (sound performance) in an AMCA-accredited laboratory.

* + - 1. COORDINATION
				1. Coordinate sizes and locations of supports required for fan units.
				2. Coordinate sizes and locations of equipment supports, wall boxes, and wall penetrations.
			2. FIELD CONDITIONS
				1. Handling and Storage: Handle and store fan units in accordance with manufacturer's published instructions. Examine units upon delivery for damage. Store units protected from weather.
			3. WARRANTY

Specifier: Consult Aerovent for available special Project-specific warranties.

* + - * 1. Manufacturer's Warranty: Manufacturer's standard form in which manufacturer agrees to furnish replacement components for fan units that demonstrate defects in workmanship or materials under normal use within warranty period specified.

Warranty Period: 12 months from startup or 18 months from shipment by manufacturer, whichever first occurs.

1. PRODUCTS
	* + 1. MANUFACTURER
				1. Basis-of-Design Manufacturer: Provide fan units manufactured by **Aerovent**, Minneapolis MN; (763) 551-7500; email: aerovent\_sales@aerovent.com; website: [www.aerovent.com](http://www.tcf.com).
				2. Source Limitations: Obtain centrifugal wall ventilators from a single manufacturer.
			2. PERFORMANCE REQUIREMENTS
				1. Fan Performance Ratings: [Project site elevation-based] [Sea level elevation-based].
				2. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70.
			3. FIBERGLASS CENTRIFUGAL WALL VENTILATORS
				1. Direct-Driven, Fiberglass Centrifugal Wall Ventilators: Centrifugal fan units, configured for wall exhaust of moisture-laden, corrosive, or chemically contaminated exhaust air for rooftop discharge.

Basis of Design Product: **Aerovent, Model ASA**.

Permanently attach nameplate displaying serial number and unit information.

* + - * 1. Fan Capacities, Characteristics, and Configuration: Refer to Drawing schedule.
				2. Motor Mount Assemblies: Provide motor mount assemblies fabricated of heavy gauge fiberglass.
				3. Wheel: Centrifugal, backward inclined, flat blade polypropylene on cast aluminum hub. Include matching inlet venturi.

Statically and dynamically balance wheel.

* + - * 1. Housing: Heavy gauge fiberglass construction of shroud, cover, and motor bands. Include fiberglass additives to limit flame spread rating to 25, when tested in accordance with ASTM E84.

Specifier: Standard bird screen is PVC coated. Stainless steel screen is optional.

Provide 1/2 x 1/2 inch (13 x 13 mm) [PVC coated] [304 stainless steel] wire bird screen at fan outlet.

* + - * 1. Motors: Comply with NEMA MG-1 for designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Division 23 section "Common Motor Requirements for HVAC Equipment." Locate motor outside airstream.

Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

Extend motor leads at factory through airtight vinyl coated flexible metal conduit and wire to non-used disconnect switch contained within terminal junction box mounted under fan motor cover. Provide conduit chase constructed of airtight vinyl coated flexible metal conduit to the motor compartment for field supply conductors.

Specifier: Select motor electrical data in following subparagraphs, or show this data on the drawing fan schedule. Do not show the data in both places.

Electrical Data:

Voltage: [115] [208] [230] [277] [460] [575] [\_\_\_\_\_] VAC; [1] [3] phase; 60 Hz.

Full Load Amps: [\_\_\_\_\_] A.

Enclosure Type: [Open, Drip Proof (ODP)] [Totally enclosed, fan cooled].

Specifier: For motors controlled by VFDs, retain following subparagraph.

Provide premium efficiency motor, suitable for inverter duty.

Provide unfused disconnect switch, NEMA [1] [3R] [4], selected in accordance with Division 26 section "Enclosed Switches."

Specifier: Retain the first following paragraph for all except explosion proof components. Retain the second following paragraph for explosion proof components only.

Factory mount and wire disconnect switch.

Ship motor and disconnect loose for field mounting and wiring.

Specifier: The standard finish color for FRP parts is beige, grey is optional. Those that follow are optional finishes. Select finish that is required.

* + - * 1. Finish: Fiberglass reinforced plastic parts to be [beige] [grey] in color. All carbon steel components shall be cleaned and chemically treated by a phosphatizing process and shall then be coated with black epoxy.
				2. Accessories:

Specifier: When backdraft dampers are required, select one of the following two paragraphs. If both types of dampers are required on various units, coordinate with fan schedule on drawings to indicate which damper type is associated with each fan.

For the following paragraph, the standard material is PVC. Aluminum is optional.

Backdraft Damper, Gravity Type: [PVC] [Aluminum] construction, parallel-blade type. Adjust backdraft damper to close when fan is not running.

Backdraft Damper, Motorized Type: Aluminum construction, parallel-blade type. Adjust backdraft damper to close when fan is not running.

Specifier: Retain the following paragraph for motorized backdraft dampers, and select required voltage for actuator power.

Backdraft damper actuator suitable for [115] [208] [230] [460] [575] VAC, single phase. [Provide transformer for [575] V actuator.]

Insect screen: 304 stainless steel wire.

Stainless Steel Nameplate: Attach to fan housing.

* + - 1. SOURCE QUALITY CONTROL
				1. Factory Run Test: Test run assembled fan units prior to shipment at specified operating speed or maximum RPM allowed. Statically and dynamically balance each wheel in accordance with AMCA 204 "Balance Quality and Vibration Levels for Fans" to Fan Application Category BV-3, Balance Quality Grade G6.3. Obtain balance readings by electronic equipment in the axial, vertical, and horizontal directions on each set of bearings.

Submit report of factory run test.

1. EXECUTION
	* + 1. EXAMINATION
				1. Examine areas to receive fans. Notify Engineer regarding conditions that may adversely affect installation, operation, or maintenance of fans. Proceed with installation once conditions are in accordance with manufacturer's published instructions.
			2. PROTECTION
				1. Protect adjacent construction and finished surfaces during installation and testing.
				2. Except for operational testing, do not operate fan during construction.
			3. INSTALLATION
				1. Install fans in accordance with Contract documents and manufacturer's published instructions.

Specifier: Insert applicable installation requirements for vibration, seismic, and high wind design if applicable to installation.

* + - * 1. Install fan units with adequate clearances for service and maintenance.

Specifier: Coordinate duct installation and specialty arrangements with schematics on Drawings and with requirements specified in duct systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

* + - * 1. Duct Connections: Drawings indicate general arrangement of ducts and duct accessories. Where indicated on Drawings, [install factory-furnished companion flanges and] make final duct connections with flexible connectors. Flexible connectors are specified in Division 23 section "Air Duct Accessories."

Install connecting ducts with adequate clearances for service and maintenance.

* + - * 1. Electrical Connections: Connect wiring in accordance with NFPA 70 and Division 26 section "Low-Voltage Electrical Power Conductors and Cables."

Ground and bond equipment according to Division 26 section "Grounding and Bonding for Electrical Systems."

* + - * 1. Equipment Identification: Label units according to Division 23 section "Identification for HVAC Piping and Equipment."
			1. FIELD QUALITY CONTROL

Specifier: Select option in paragraph below to define the party responsible for final tests and inspections to be performed.

* + - * 1. [Owner will retain] [Contractor shall retain] qualified testing agency to perform field tests and inspections.

Specifier: Retain first paragraph below to describe tests and inspections to be performed.

* + - * 1. Tests and Inspections:

Verify that unit is secured to supports, and that duct and electrical connections are complete. Verify that proper thermal-overload protection is installed in motors, starters, and disconnect switches.

Verify that cleaning and adjusting are complete.

Verify proper motor rotation direction, and verify fan wheel free rotation and smooth bearing operation.

Verify that manual and automatic volume control, and fire and smoke dampers in connected ductwork systems are in fully open position.

Disable automatic temperature-control actuators, energize motor, adjust fan to indicated rpm, and measure and record motor voltage and amperage.

Shut unit down and reconnect automatic temperature-control actuators.

Remove and replace malfunctioning units and retest as specified above.

* + - * 1. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.
				2. Submit test and inspection reports.
			1. ADJUSTING AND CLEANING
				1. Adjust, clean, and maintain installed fan units in accordance with manufacturer's published instructions.

END OF SECTION