****

**Aerovent Guide Specification  
Tubeaxial Fans, Direct Drive: Model BSTA**

**Aerovent Model BSTA Series, Tubeaxial Fans** are specifically designed for cost effective, reliable air movement in commercial and light industrial ducted and non-ducted applications. Direct drive models are available with cast aluminum impellers to meet specific application requirements. Model BSTA fans offer superior air and sound performance and the AMCA certified rating seal for air and sound and is UL/cUL 705 listed.

**Application**

Model BSTA is available in direct drive configurations and mounts both vertically and horizontally, allowing for numerous applications with multiple mounting arrangements.

Sizes (impeller diameters): 14 to 48 inches (356 mm to 1,219 mm)

Airflow: 870to 42,700 CFM (1,478 to 72,547 m3/hour)

Static Pressure: Up to 1.5 inches wg (373 Pa)

Aerovent is a leading designer and manufacturer of high quality industrial air moving equipment. Aerovent has extensive industry experience and years of active research, offering customers flexibility in fan design and construction along with superior service and state-of-the-art technology. With an unmatched variety of axial impellers and centrifugal fan wheels, every fan is built to the customer’s specific needs. This comprehensive selection of products and materials makes Aerovent the ideal choice for a diverse range of industry applications, including: Pulp & Paper, Automotive, Metal & Minerals, Mining, Power Generation, Agricultural, Marine and Water Treatment.

Aerovent occupies over 1,000,000 sq. ft. of manufacturing space in the U.S. Headquarters are located in Minneapolis, Minnesota, which houses the management, sales and marketing, accounting, human resources, material management, engineering personnel, as well as a state-of-the-art AMCA accredited testing lab.

We recommend you consult with your Aerovent Sales Representative, who can be contacted through: Aerovent, Minneapolis MN; (763) 551-7500; email: [aerovent\_sales@aerovent.com](mailto:tcf_sales@tcf.com); [www.aerovent.com](http://www.tcf.com).

This document Copyright© 2017 Aerovent

SECTION 23 34 13.01 – TUBEAXIAL FANS

1. GENERAL
   * + 1. SUMMARY
          1. Section includes direct-drive fixed or adjustable pitch airfoil axial fans.
       2. REFERENCE STANDARDS
          1. Air Movement and Control Association International, Inc. (AMCA): [www.amca.org](http://www.amca.org):

AMCA Standard 204 - Balance Quality and Vibration Levels for Fans

AMCA Standard 205 - Energy Efficiency Classification for Fans

AMCA Standard 210 - ASHRAE 51 - Laboratory Methods of Testing Fans for Certified Aerodynamic Performance Rating

AMCA Publication 211 - Certified Ratings Program - Product Rating Manual for Fan Air Performance

AMCA Standard 300 - Reverberant Room Method for Sound Testing of Fans

AMCA Publication 311 - Certified Ratings Program - Product Rating Manual For Fan Sound Performance

* + - * 1. National Electrical Manufacturers Association (NEMA): [www.nema.org](http://www.nema.org):

NEMA MG 1 – Motors and Generators

* + - * 1. National Fire Protection Association (NFPA): [www.nfpa.org](http://www.nfpa.org):

NFPA 70 - National Electric Code

* + - * 1. Underwriters Laboratories, Inc. / Underwriters Laboratories of Canada (UL/cUL): [www.ul.com](http://www.ul.com):

UL/cUL 705 - Standard for Power Ventilators

* + - 1. ACTION SUBMITTALS
         1. Product Data: Include the following:

Rated capacities and operating characteristics.

Fan Performance Data: Fan performance curves with flow, static pressure and horsepower.

Sound Performance Data: Fan sound power levels in eight octave bands and, A-weighted overall sound power level or sone values.

Motor ratings and electrical characteristics.

Furnished specialty components.

Specified accessories.

Dimensioned standard drawings indicating dimensions, weights, and attachments to other work.

Specifier: If Contractor will be required to provide engineering drawings and calculations for vibration, seismic, or high wind design, insert requirements here.

* + - 1. INFORMATIONAL SUBMITTALS
         1. Source quality-control reports.
         2. Field quality-control reports.
         3. ISO-9001 certificate.
      2. CLOSEOUT SUBMITTALS
         1. Operation and Maintenance Data: Include routine maintenance, adjustment requirements, safety information, and troubleshooting guide.
      3. QUALITY ASSURANCE
         1. Manufacturer Qualifications: Approved ISO 9001-compliant manufacturer listed in this Section with minimum 10 years' experience in manufacture of similar products in successful use in similar applications, and with an ASME NQA-1 compliant Program.

Specifier: Retain paragraph below if Owner allows substitutions but requires strict control over qualifying of substitutions.

Approval of Comparable Products: Submit the following in accordance with project substitution requirements, within time allowed for substitution review:

Product data, including certified independent test data indicating compliance with requirements.

Project references: Minimum of 5 installations not less than 5 years old, with Owner contact information.

Sample warranty.

Substitutions following award of contract are not allowed except as stipulated in Division 01 General Requirements.

Approved manufacturers must meet separate requirements of Submittals Article.

* + - * 1. AMCA Compliance:

Provide fan types tested in accordance with AMCA Standard 210 (air performance) and AMCA Standard 300 (sound performance) in an AMCA-accredited laboratory.

Provide fan units rated according to AMCA Standard 211 (air performance) and AMCA Standard 311 (sound performance).

Provide fan units rated according to AMCA Standard 205 (fan efficiency grade).

* + - 1. COORDINATION
         1. Coordinate sizes and locations of supports required for fan units.
         2. Coordinate sizes and locations of equipment supports, roof curbs, and roof penetrations.
      2. FIELD CONDITIONS
         1. Handling and Storage: Handle and store fan units in accordance with manufacturer's published instructions. Examine units upon delivery for damage. Store units protected from weather.
      3. WARRANTY

Specifier: Consult Aerovent for available special Project-specific warranties.

* + - * 1. Manufacturer's Warranty: Manufacturer's standard form in which manufacturer agrees to furnish replacement components for fan units that demonstrate defects in workmanship or materials under normal use within warranty period specified.

Warranty Period: 12 months from startup or 18 months from shipment by manufacturer, whichever first occurs.

1. PRODUCTS
   * + 1. MANUFACTURER
          1. Basis-of-Design Manufacturer: Provide fan units manufactured by Aerovent, Minneapolis MN; (763) 551-7500; email: [aerovent\_sales@aerovent.com](mailto:tcf_sales@tcf.com); website: [www.aerovent.com](http://www.tcf.com).
          2. Source Limitations: Obtain mixed flow fans from a single manufacturer.
       2. PERFORMANCE REQUIREMENTS
          1. Fan Performance Ratings: [Project site elevation-based] [Sea level elevation-based].
          2. AMCA Compliance: Provide units that bear the AMCA-Certified Ratings Seal.
          3. Compliance:

Classified under AMCA Standard 205.

Provide units listed in accordance with UL/cUL 705.

* + - * 1. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70.
      1. AXIAL FLOW FANS
         1. Direct-driven adjustable pitch airfoil axial fans, configured for horizontal or vertical flow of relatively clean air for Heating, Ventilating, and Air-Conditioning (HVAC) applications, for air containing dirt, moisture, or hazardous fumes, or for air at elevated temperatures.

Basis of Design Product: **Aerovent, Model BSTA**.

Permanently attach nameplate displaying serial number and unit information.

* + - * 1. Fan Capacities, Characteristics, and Configuration: Refer to Drawing schedule.
        2. Fan Impeller: [Die cast aluminum, adjustable-pitch, [4] [5] [6] [8]-blade] mounted in cast aluminum hubs.

Hub Attachment to Shaft: Taper-lock bushing.

Specifier: Retain the following paragraph for impellers with aluminum blades.

Statically and dynamically balance impeller when fabricated, and again after fan unit has been assembled.

* + - * 1. Casing: Formed ASTM A-569 low carbon hot rolled steel with continuously welded seams. Apply [metalized vinyl] [aluminum] [stainless steel] nameplate.
        2. Motors: Comply with NEMA MG-1 for designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Division 23 section "Common Motor Requirements for HVAC Equipment."

Manufactured in accordance with current applicable standards of IEEE and NEMA.

Foot-mounted, NEMA standard, rated for continuous duty with class “B” insulation.

Provide ball bearings with external grease fittings.

Specifier: Select motor electrical data in following subparagraphs, or show this data on the drawing fan schedule. Do not show the data in both places.

Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

Electrical Data:

Voltage: [115] [208] [230] [460] [575] [\_\_\_\_\_] VAC; [1] [3] phase; 60 Hz.

Full Load Amps: [\_\_\_\_\_] A.

Specifier: Standard motor has ODP enclosure. Select other options as required for the project.

Enclosure Type: [Open, Drip Proof (ODP)] [Totally Enclosed Fan Cooled (TEFC)] [Explosion Proof (XP)].

Specifier: Select motor enclosure type in first following subparagraph. For motors controlled by VFDs, retain second following subparagraph.

Enclosure Type: [Open, Drip Proof (ODP)] [Totally Enclosed Fan Cooled (TEFC)] [Explosion Proof] [ATEX].

Provide motors that comply with the Energy Independence and Security Act of 2007 (EISA).

When controlled with a Variable Frequency Drive (VFD), provide premium efficiency motors suitable for inverter duty use.

Specifier: If factory disconnect is required, select NEMA enclosure rating in following paragraph, and select one subparagraph below to specify factory or field mounting.

Retain second subparagraph when NEMA 7/9 (explosion proof) option is selected.

Provide unfused disconnect switch, NEMA [1] [3R] [4] [4X] [7/9 explosion proof], selected in accordance with Division 26 section "Enclosed Switches."

Factory mount and wire disconnect switch.

Ship disconnect switch loose for field mounting and wiring.

Motor Mounting Platform: Heavy-duty motor mounting platform.

* + - * 1. Finishes:

After fabrication, clean and chemically pretreat steel parts by phosphatization.

Specifier: Specifier: The first paragraph below is manufacturer's standard finish. Those that follow are optional finishes. Select finish that is required.

Apply two coats

[Enamel, Gray]

[Enamel, Color Matched]

[Epoxy, Black]

[Phenolic Heresite, Gray]

[Carbocoat 30, Black]

[Transcoat 161, Black].

* + - * 1. Accessories:

Specifier: Accessories listed in subparagraphs below are optional Aerovent features for this unit. Consult Aerovent representative for recommended options based upon Project requirements.

Companion Flange: Provide slip on ductwork companion flanges, rolled angle rings punched to match standard fan inlet or outlet flange.

Specifier: Retain the following paragraph if factory furnished base mounting or hanging brackets are required. Brackets for horizontal and vertical mounting are available.

Provide mounting brackets for vertical and horizontal installation.

Access Door, Bolted: Provide access door with bolted cover to allow inspection and maintenance of internal fan components.

Externally Mounted Conduit Box.

Inlet Bell: Provide spun steel inlet bell with pre-punched flange holes to enable bolted connection to fan inlet. Finish with manufacturer's standard paint.

[Inlet] [Outlet] Guards: Removable, welded wire screens.

Specifier: Retain paragraph and subparagraph below, and coordinate options with project design.

Provide [spring] [neoprene-in-shear] vibration isolators, [and seismic restraints] in accordance with fan manufacturer's requirements, and Division 23, Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

Spring Isolators: Select for [1 inch (25.4 mm)] [2 inch (51 mm)] deflection.

* + - 1. SOURCE QUALITY CONTROL
         1. Factory Run Test: Test run assembled fan units prior to shipment at specified operating speed or maximum RPM allowed. Statically and dynamically balance each impeller in accordance with AMCA 204 "Balance Quality and Vibration Levels for Fans" to Fan Application Category BV-3, Balance Quality Grade G6.3. Obtain balance readings by electronic equipment in the axial, vertical, and horizontal directions on each set of bearings.

Submit report of factory run test.

1. EXECUTION
   * + 1. EXAMINATION
          1. Examine areas to receive fans. Notify Engineer regarding conditions that may adversely affect installation, operation, or maintenance of fans. Proceed with installation once conditions are in accordance with manufacturer's published instructions.
       2. PROTECTION
          1. Protect adjacent construction and finished surfaces during installation and testing.
          2. Except for operational testing, do not operate fan during construction.
       3. INSTALLATION
          1. Install fans in accordance with Contract documents and manufacturer's published instructions.

Specifier: Insert applicable installation requirements for vibration, seismic, and high wind design if applicable to installation.

* + - * 1. Install fan units with adequate clearances for service and maintenance.

Specifier: Coordinate duct installation and specialty arrangements with schematics on Drawings and with requirements specified in duct systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

* + - * 1. Duct Connections: Drawings indicate general arrangement of ducts and duct accessories. Where indicated on Drawings, [install factory-furnished companion flanges and] make final duct connections with flexible connectors. Flexible connectors are specified in Division 23 section "Air Duct Accessories."

Install connecting ducts with adequate clearances for service and maintenance.

* + - * 1. Electrical Connections: Connect wiring in accordance with NFPA 70 and Division 26 section "Low-Voltage Electrical Power Conductors and Cables."

Ground and bond equipment according to Division 26 section "Grounding and Bonding for Electrical Systems."

* + - * 1. Equipment Identification: Label units according to Division 23 section "Identification for HVAC Piping and Equipment."
      1. FIELD QUALITY CONTROL

Specifier: Select option in paragraph below to define the party responsible for final tests and inspections to be performed.

* + - * 1. [Owner will retain] [Contractor shall retain] qualified testing agency to perform field tests and inspections.

Specifier: Retain first paragraph below to describe tests and inspections to be performed.

* + - * 1. Tests and Inspections:

Verify that unit is secured to supports, and that duct and electrical connections are complete. Verify that proper thermal-overload protection is installed in motors, starters, and disconnect switches.

Verify that cleaning and adjusting are complete.

Verify proper motor rotation direction, and verify fan impeller free rotation and smooth bearing operation.

Verify that manual and automatic volume control, and fire and smoke dampers in connected ductwork systems are in fully open position.

Disable automatic temperature-control actuators, energize motor, adjust fan to indicated rpm, and measure and record motor voltage and amperage.

Shut unit down and reconnect automatic temperature-control actuators.

Remove and replace malfunctioning units and retest as specified above.

* + - * 1. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.
        2. Submit test and inspection reports.
      1. ADJUSTING AND CLEANING
         1. Adjust, clean, and maintain installed fan units in accordance with manufacturer's published instructions.

END OF SECTION